## Heat Pump Terms of Use
Cool Prop must be installed (see work sheet CoolProp_Installation)
Terms of Use Heat_Pump Sheet
(c) University of Innsbruck, Unit of Energy Efficient Building
Technikerstrasse 13, A-6020 Innsbruck, Austria
Wolfgang Streicher
wolfgang.streicher@uibk.ac.at
Inputs: Only | yellow fields
FREEWARE: but please cite when it is used
It is NOT allowed to sell this software commercially
If you use plots make sure that the citation of the University of Innsbruck is readable or attached to the graph
There is NO liabilty for the use, calculation and the results
Please be sure, that data is harmonized, e.g. negative dTlog will be shown
There is no support team behind the tools, please ask only in very urgent situations

## Heat_Pump
[8 empty] | INPUT Heat Pump Cycle |  |  |  |  | Key Figures |  |  |  | Pinch points
Saturation Table for | [6 empty] | R134a | Material Heat Sink |  | Water |  |  | T_condensation | °C | 38 |  | T-Compr_out | °C | 53.378
[8 empty] | T sink_out | °C | 35 | 308.15 |  | T_evaporation | °C | -1
Temperature | Temperature | Temperat. | Pressure | Sat. liquid | Sat. vapor | Sat. liquid. | Sat. Vapor | T sink In | °C | 30 | 303.15 |  | COPcarnot,h So_i-Si_o |  | 11.0054 |  | Condenser
|  | until krit. |  | density | density | Enthalpy | Enthalpy | Material Heat Source |  | Air |  |  | COPch Refr,E-K | - | 7.9782 |  | Delta T Pinch | °C | 3.4478
°C | K | °C | kPa | kg/m³ | kg/m³ | kJ/kg | kJ/kg | T source_in | °C | 7 | 280.15 |  | COP h_Refr | - | 5.6846 |  | Delta T Si-Refr_a | °C | 5
[8 empty] | T source_out | °C | 2 | 275.15 |  | COP c_Refr | - | 4.6846 |  | dtLog desuperheating | °C | 8.922
[13 empty] | Qdot condenser | kW | 10 |  | dtlog condensation | °C | 5.3621 | bar: °C
-30 | 243.15 | -30 | 84.3777 | 1388.4017 | 4.4259 | 160.792 | 380.3186 | dT 5 - sink_out | K | 3 |  |  | Qdot evaporator | kW | 8.2408 |  | dtlog subcooling | °C | 6.3313
-20 | 253.15 | -20 | 132.735 | 1358.2654 | 6.7845 | 173.6357 | 386.5543 | dT source_in -3 | K | 3 |  |  | Qdot compr. | kW | 1.7592 |  | Evaporator
-10 | 263.15 | -10 | 200.6033 | 1327.1262 | 10.0412 | 186.6966 | 392.6649 | dT cond_subcool 6-7 | K | 3 |  |  | Qel kompr | kW | 1.9546 |  | Delta T So-Ref_a | °C | 3
0 | 273.15 | 0 | 292.8032 | 1294.777 | 14.4282 | 200 | 398.6035 | dT cvap_superh. 3-2 | K | 5 |  |  | Mdot KM | kg/s | 0.053689 |  | Delta T So_1-Ref._e | °C | 3
10 | 283.15 | 10 | 414.6075 | 1260.9577 | 20.2258 | 213.5772 | 404.3181 | [5 empty] | COP h-el | - | 5.1161 |  | dtLog evaporation | °C | 5.044
20 | 293.15 | 20 | 571.7069 | 1225.3334 | 27.7803 | 227.4677 | 409.7483 | Power Cond | kW | 10 |  |  | COP c_el | - | 4.2161 |  | dTlog superheating | °C | 5.044
30 | 303.15 | 30 | 770.1963 | 1187.4619 | 37.5353 | 241.7224 | 414.8185 | eta_is compressor | - | 0.8 |  |  | COP h_el/COPc SoiSio |  | 0.46487
40 | 313.15 | 40 | 1016.593 | 1146.7392 | 50.085 | 256.4092 | 419.4285 | eta_el compressor | - | 0.9 |  |  | cp_Sink | J/kg,k | 4177.035 |  | rho_Sink | kg/m³ | 994.8675
50 | 323.15 | 50 | 1317.9055 | 1102.3059 | 66.2716 | 271.6232 | 423.437 | [5 empty] | cp_Source | J/kg,k | 1023.2622 |  | rho_Source | kg/m³ | 1.2717
60 | 333.15 | 60 | 1681.7842 | 1052.8622 | 87.3794 | 287.5047 | 426.6296 | R134a | GWP | 1430 |  |  | Mdot_Sink | kg/s | 0.47881 | kg/h | 1723.7107 | m³/h | 1.7326
70 | 343.15 | 70 | 2116.8257 | 996.2482 | 115.5715 | 304.2824 | 428.6498 | [5 empty] | Mdot_Source | kg/s | 1.6107 | kg/h | 5798.5228 | m³/h | 4559.5821
80 | 353.15 | 80 | 2633.2033 | 928.2444 | 155.0784 | 322.3902 | 428.8136
90 | 363.15 | 90 | 3244.1826 | 837.826 | 216.7608 | 342.9282 | 425.4156 | Refrigerant Cycle |  | 1 | 2 | 3 | 4a | 4 | 5 | 6 | 7 |  | Water
100 | 373.15 | 100 | 3975.3933 | 651.1145 | 393.0457 | 373.3042 | 404.4594 |  |  | Ev._in | Ev.Tevap | Ev._out | Compr_o_is | cond_in | cond_Tcond. | Cond_liq | Cond_out |  | Air
110 | 374.21 | 101.06 | 4059.1115 | 511.9 | 511.9 | 389.6389 | 389.6389 | T | °C | -1 | -1 | 4 | 47.2248 | 53.378 | 38 | 38 | 35
120 | 374.21 | 101.06 | 4059.1115 | 511.9 | 511.9 | 389.6389 | 389.6389 | T | K | 272.15 | 272.15 | 277.15 | 320.3748 | 326.528 | 311.15 | 311.15 | 308.15
130 | 374.21 | 101.06 | 4059.1115 | 511.9 | 511.9 | 389.6389 | 389.6389 | p | Pa | 282341.3617 | 282341.3617 | 282341.3617 | 963152.6566 | 963152.6566 | 963152.6566 | 963152.6566 | 963152.6566 | cp*dt | h=f(T,P)
140 | 374.21 | 101.06 | 4059.1115 | 511.9 | 511.9 | 389.6389 | 389.6389 |  | bar | 2.8234 | 2.8234 | 2.8234 | 9.6315 | 9.6315 | 9.6315 | 9.6315 | 9.6315
150 | 374.21 | 101.06 | 4059.1115 | 511.9 | 511.9 | 389.6389 | 389.6389 | h | J/kg | 248972.2965 | 398018.7669 | 402464.2808 | 428676.7393 | 435229.8539 | 418549.3385 | 253433.2438 | 248972.2965 | 248972.2965 | 248998.7852
160 | 374.21 | 101.06 | 4059.1115 | 511.9 | 511.9 | 389.6389 | 389.6389 | S | J/kg | 3: 1743.8344; 4a: 1743.8344
170 | 374.21 | 101.06 | 4059.1115 | 511.9 | 511.9 | 389.6389 | 389.6389 | cp | J/kgK | 7: 1486.9824
180 | 374.21 | 101.06 | 4059.1115 | 511.9 | 511.9 | 389.6389 | 389.6389
190 | 374.21 | 101.06 | 4059.1115 | 511.9 | 511.9 | 389.6389 | 389.6389 |  | Point | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 1
200 | 374.21 | 101.06 | 4059.1115 | 511.9 | 511.9 | 389.6389 | 389.6389 | Grafic |  | Evap_in | Ev.Tevap | Evap_out | Cond_in | Cond_vap | Cond_liq | Cond_out | Evap_in
210 | 374.21 | 101.06 | 4059.1115 | 511.9 | 511.9 | 389.6389 | 389.6389 | T | °C | -1 | -1 | 4 | 53.378 | 38 | 38 | 35 | -1
220 | 374.21 | 101.06 | 4059.1115 | 511.9 | 511.9 | 389.6389 | 389.6389 | p | kPa | 282.3414 | 282.3414 | 282.3414 | 963.1527 | 963.1527 | 963.1527 | 963.1527 | 282.3414
230 | 374.21 | 101.06 | 4059.1115 | 511.9 | 511.9 | 389.6389 | 389.6389 | h | kJ/kg | 248.9723 | 398.0188 | 402.4643 | 435.2299 | 418.5493 | 253.4332 | 248.9723 | 248.9723
240 | 374.21 | 101.06 | 4059.1115 | 511.9 | 511.9 | 389.6389 | 389.6389
250 | 374.21 | 101.06 | 4059.1115 | 511.9 | 511.9 | 389.6389 | 389.6389 |  |  | 1: in; 2: out
260 | 374.21 | 101.06 | 4059.1115 | 511.9 | 511.9 | 389.6389 | 389.6389 | Source | °C | 1: 2; 2: 7
270 | 374.21 | 101.06 | 4059.1115 | 511.9 | 511.9 | 389.6389 | 389.6389 |  | kJ/kg | 1: 248.9723; 2: 402.4643
280 | 374.21 | 101.06 | 4059.1115 | 511.9 | 511.9 | 389.6389 | 389.6389 | Sink | °C | 1: 35; 2: 30
290 | 374.21 | 101.06 | 4059.1115 | 511.9 | 511.9 | 389.6389 | 389.6389 |  | kJ/kg | 1: 435.2299; 2: 248.9723
300 | 374.21 | 101.06 | 4059.1115 | 511.9 | 511.9 | 389.6389 | 389.6389
310 | 374.21 | 101.06 | 4059.1115 | 511.9 | 511.9 | 389.6389 | 389.6389 | Pinch point | bar: 1 to 5
320 | 374.21 | 101.06 | 4059.1115 | 511.9 | 511.9 | 389.6389 | 389.6389 | Condenser |  | 3: Evaporator
330 | 374.21 | 101.06 | 4059.1115 | 511.9 | 511.9 | 389.6389 | 389.6389 | Qdot desuperheat | kW | 1: 0.89556
340 | 374.21 | 101.06 | 4059.1115 | 511.9 | 511.9 | 389.6389 | 389.6389 | Tsink, pinch | °C | 1: 34.5522
350 | 374.21 | 101.06 | 4059.1115 | 511.9 | 511.9 | 389.6389 | 389.6389 | Trefr pinch | °C | 1: 38
360 | 374.21 | 101.06 | 4059.1115 | 511.9 | 511.9 | 389.6389 | 389.6389 | Delta T Pinch | °C | 1: 3.4478; 3: Delta T So-Ref_a; 4: °C; 5: 3
101.06 | 374.21 | 101.06 | 4059.28 | 511.9 | 511.9 | 389.6389 | 389.6389 | Delta T Si-Refr_a | °C | 1: 5; 3: Delta T So_1-Ref._e; 4: °C; 5: 3
[8 empty] | Qdot Subcooling | kW | 1: 0.2395; 3: Qdot Evaporation; 4: kW; 5: 0.23868
[8 empty] | Tsink condensation | °C | 1: 30.1198; 3: Tsource_Evap_ee; 4: °C; 5: 6.8552
[8 empty] | Delta Tsink cond | °C | 1: 7.8802; 3: Delta T source_Evapor.; 4: °C; 5: 7.8552

## CoolProp_Installation
CoolProp
Installation
Installation Instructions
Automatic Installation
Download CoolProp Windows installer from
https://sourceforge.net/projects/coolprop/files/CoolProp/6.8.0/Installers/Windows/
an let it run. You may have to tell Excel, where CoolProp.xlam is installed.
When you use the coolprop.exe installer, the xlam-File can be found at "C:\Users\%USERPROFILE%\AppData\Roaming\Microsoft\AddIns"
In some cases it can be necessary to restart Excel during this process.
Download files eperately
a) Download the CoolProp.dll and CoolProp_x64.dll files and place them in a folder called C:\CoolProp*
b) Download the CoolProp.xlam file and place it in a convenient location
c) Install the CoolProp Add-in from the Excel Options menu, Manage Add-ins
1) Open Excel
2) Go to the menu File→Options→Add-Ins
3) At the bottom of the panel, select Manage: Excel Add-ins, then click the Go… button.
4) Click the browse button on the Add-in Manager panel.
5) Browse to the file CoolProp.xlam that you copied above in step (b).
6) Make sure the CoolProp Add-in is selected (box checked) and close the add-in manager.
d) Open the file TextExcel.xlsx (this file) and try to re-evaluate one of the formula cells on the Sample Calcs tab. The CoolProp formulas should all be working.
*Alternate CoolProp Location
If you need to place the CoolProp DLL files in a location other than on the C: drive, follow these instructions:
a) Download the CoolProp.dll and CollProp_64.dll files and place them in CoolProp directory in a reachable location
b) Open CoolProp.xlam
c) You will get an Excel error - File not found: C:\CoolProp\CoolProp.dll
d) Clicking Ok on the error dialog only brings up another. Try pressing and holding the <Enter> key until the errors go away
e) Go to File ¦ Options on the main menu and select Customize Ribbon from the Excel Options panel menu
1) In the right hand pane under Main Tabs, make sure that the box in front of Developer is checked
2) Press OK
f) Under the Developer menu, select Visual Basic to bring up the visual basic editor
1) Select Edit ¦ Replace… from the main menu
2) Enter the following on the panel
Find What: C:\CoolProp\CoolProp.dll
Replace With: (new location)
3) Press the Replace All button
4) Repeat for C:\CoolProp\CoolProp_64.dll
g) Press the Save button (disk image) or File ¦ Save
h) Press File ¦ Close and Return to Excel
i) Press <Alt>-<Ctrl>-<Shift>-F9 to recalculate the entire workshee on the Sample Calcs tab. All formulas should now be working.

## Sample Calcs
CoolProp
Example Calculations
Function Usage | Units | COOLPROP | Expected value | Function Call
Critical temperature of R410A: | K | 344.494 | 344.494 | =Props1SI("R410A";"Tcrit")
Critical density of propane: | kg/m³ | 220.4781 | 220.4781 | =Props1SI("Propane";"rhocrit")
Density of Nitrogen at STP: | kg/m³ | 1.2504 | 1.2504 | =PropsSI("Dmass","T",298.15,"P",101325,"HEOS::Nitrogen")
Density of Air at STP: | kg/m³ | 1.2931 | 1.2931 | =PropsSI("Dmass","T",298.15,"P",101325,"HEOS::Air")
Boiling point of water at 1 atm: | °C | 99.9743 | 99.9743 | =PropsSI("T","P",101325,"Q",0,"HEOS::Water")-273.15
Boiling point of water at 1 atm: | °C | #VALUE! | 99.9743 | =PropsSI("T","P",101325,"Q",0,"REFPROP::Water")-273.15
Example of an error: |  | Neither input to Props1SI [A,B] is a valid fluid |  | =Props1SI("A","B")
CoolProp DLL version installed: |  | 6.6.0 | [current version] | =get_global_param_string("version")
CoolProp Git Revision: |  | ba21c74fd1c3a4934bbecbf459936983dec424c2 |  | =get_global_param_string("gitrevision")
Phase Determination
Water phase @ RT |  | liquid | liquid | =PhaseSI("T",293.15,"P",101325,"Water")
Water phase @ 400 K and 1 atm |  | gas | gas | =PhaseSI("T",400,"P",101325,"Water")
Water phase @ 400 K and 30 MPa |  | supercritical_liquid | supercritical_liquid | =PhaseSI("T",400,"P",30e6,"Water")
Water phase @ 1030 K and 10 MPa |  | supercritical_gas | supercritical_gas | =PhaseSI("T",1030,"P",10e6,"Water")
Water phase @ 1030 K and 30 MPa |  | supercritical | supercritical | =PhaseSI("T",1030,"P",30e6,"Water")
Mixtures
Components | mole fraction
Nitrogen | 0.7809
Oxygen | 0.2095
Argon | 0.0093
CO2 | 0.00039
Dewpoint of dry air at 1 atm: | K | 78.9334 | 78.9334 | =PropsSI("T","P",101325,"Q",0,"HEOS::"&MixtureString(A17:A20,B17:B20))
Density of dry Air at STP: | kg/m³ | 1.2932 | 1.2932 | =PropsSI("D","T",273.15,"P",101325,"HEOS::"&MixtureString(A17:A20,B17:B20))
Humid Air Properties | Units | COOLPROP | Expected value | Function Call
Dewpoint of dry Air at 1 atm: | K | 149.3954 | 149.3954 | =HAPropsSI("D","T",293.15,"P",101325,"R",0)
Dewpoint of air at 1 atm, 50% humidity: | K | 282.4244 | 282.4244 | =HAPropsSI("D","T",293.15,"P",101325,"R",0.5)
Density of Dry Air at STP: | kg/m³ | 1.2931 | 1.2931 | =1/HAPropsSI("Vda","T",273.15,"P",101325,"R",0)
Density of 50% Humid Air at STP: | kg/m³ | 1.2916 | 1.2916 | =1/HAPropsSI("Vha","T",273.15,"P",101325,"R",0.5)
Enthalpy of 50% Humid Air at STP: | J/kg | 4723.4366 | 4723.4366 | =HAPropsSI("H","T",273.15,"P",101325,"R",0.5)
Temperature of Sat. Air at H=4723.44 J/kg: | K | 270.3857 | 270.3857 | =HAPropsSI("T","H",C31,"P",101325,"R",1)
* Air Temperature (T) = 20°C
Incompressible Fluid Properties | Units | COOLPROP | Expected value | Function Call
Viscosity of 20% Aqueous Ethylene Glycol: | Pa-s | 0.0013814 | 0.0013814 | =PropsSI("V","T",300,"P",101.325,"INCOMP::MEG[0.2]")
Specifi Heat of Dowtherm Q @ 500 K, 1 atm | J/kg-K | 2288.1644 | 2288.1644 | =PropsSI("C","T",500,"P",101325,"INCOMP::DowQ")
Density of Seawater @ RT, 3.5% Salinity | kg/m° | 1024.8598 | 1024.8598 | =PropsSI("V","T",300,"P",101.325,"INCOMP::MEG[0.2]")
Note on D13: Autor: This formula will not work if you do not have REFPROP installed.

## Water saturation table
Saturation Table for water
Temperature | Temperature | Pressure | Sat. Liq. | Sat. Vap. | Sat. Liq. | Sat. Vap.
|  |  | Density | Density | Enthalpy | Enthalpy
°C | K | kPa | kg/m³ | kg/m³ | kJ/kg | kJ/kg
0.01 | 273.16 | 0.61165 | 999.7925 | 0.0048546 | 0.0006122 | 2500.9152
10 | 283.15 | 1.2282 | 999.6546 | 0.0094071 | 42.0213 | 2519.2083
20 | 293.15 | 2.3393 | 998.1618 | 0.017314 | 83.9141 | 2537.4334
30 | 303.15 | 4.247 | 995.6062 | 0.030415 | 125.734 | 2555.5452
40 | 313.15 | 7.3849 | 992.1751 | 0.051242 | 167.533 | 2573.5103
50 | 323.15 | 12.3519 | 987.9962 | 0.083147 | 209.3418 | 2591.2889
60 | 333.15 | 19.9464 | 983.1602 | 0.13043 | 251.1804 | 2608.8349
70 | 343.15 | 31.2009 | 977.7337 | 0.19843 | 293.0652 | 2626.0964
80 | 353.15 | 47.4145 | 971.7662 | 0.29367 | 335.0124 | 2643.0159
90 | 363.15 | 70.1818 | 965.2953 | 0.4239 | 377.0394 | 2659.53
100 | 373.15 | 101.418 | 958.3491 | 0.59817 | 419.1662 | 2675.5699
110 | 383.15 | 143.3787 | 950.948 | 0.82693 | 461.4152 | 2691.0613
120 | 393.15 | 198.6744 | 943.1066 | 1.1221 | 503.8117 | 2705.9258
130 | 403.15 | 270.28 | 934.834 | 1.497 | 546.3836 | 2720.0811
140 | 413.15 | 361.5391 | 926.1344 | 1.9667 | 589.1617 | 2733.443
150 | 423.15 | 476.1645 | 917.0077 | 2.5481 | 632.1794 | 2745.9255
160 | 433.15 | 618.2346 | 907.4495 | 3.2596 | 675.4735 | 2757.4413
170 | 443.15 | 792.187 | 897.451 | 4.1222 | 719.0837 | 2767.9018
180 | 453.15 | 1002.8105 | 886.999 | 5.1588 | 763.0538 | 2777.2149
190 | 463.15 | 1255.2362 | 876.0757 | 6.3954 | 807.432 | 2785.2844
200 | 473.15 | 1554.9279 | 864.6581 | 7.861 | 852.2713 | 2792.007
210 | 483.15 | 1907.675 | 852.7176 | 9.5885 | 897.6312 | 2797.2698
220 | 493.15 | 2319.5862 | 840.219 | 11.6154 | 943.5787 | 2800.9471
230 | 503.15 | 2797.0875 | 827.1192 | 13.9853 | 990.1897 | 2802.8968
240 | 513.15 | 3346.9251 | 813.3656 | 16.749 | 1037.5518 | 2802.9556
250 | 523.15 | 3976.1749 | 798.8942 | 19.9668 | 1085.7675 | 2800.9331
260 | 533.15 | 4692.261 | 783.6257 | 23.7117 | 1134.958 | 2796.6032
270 | 543.15 | 5502.9868 | 767.4612 | 28.0733 | 1185.27 | 2789.6932
280 | 553.15 | 6416.5829 | 750.2752 | 33.1647 | 1236.8847 | 2779.8667
290 | 563.15 | 7441.7783 | 731.9052 | 39.1315 | 1290.0311 | 2766.6991
300 | 573.15 | 8587.9049 | 712.1356 | 46.1678 | 1345.0079 | 2749.6388
310 | 583.15 | 9865.0512 | 690.6715 | 54.5414 | 1402.2171 | 2727.9459
320 | 593.15 | 11284.2929 | 667.0938 | 64.6384 | 1462.2236 | 2700.5858
330 | 603.15 | 12858.0516 | 640.7732 | 77.0504 | 1525.8683 | 2666.0311
340 | 613.15 | 14600.6774 | 610.6676 | 92.7588 | 1594.529 | 2621.8456
350 | 623.15 | 16529.4151 | 574.7065 | 113.6056 | 1670.8899 | 2563.6367
360 | 633.15 | 18666.0066 | 527.5916 | 143.8984 | 1761.6646 | 2481.4925
370 | 643.15 | 21043.5631 | 451.4256 | 201.8393 | 1890.6872 | 2334.5183
373.946 | 647.096 | 22064 | 322 | 322 | 2084.2563 | 2084.2563

## Property Calculator
Property Calculator
Fluid Type | PureFluids
Fluid | CarbonDioxide
Output Name | V
Input Name 1 | T
Input Value 1 | 390
Input Name 2 | P
Input Value 1 | 9000
Result | 1.9174e-05

## Lists
get_global_param_string("FluidsList") ==> | 1-Butene,Acetone,Air,Ammonia,Argon,Benzene,CarbonDioxide,CarbonMonoxide,CarbonylSulfide,cis-2-Butene,CycloHexane,Cyclopentane,CycloPropane,D4,D5,D6,Deuterium,Dichloroethane,DiethylEther,DimethylCarbonate,DimethylEther,Ethane,Ethanol,EthylBenzene,Ethylene,EthyleneOxide,Fluorine,HeavyWater,Helium,HFE143m,Hydrogen,HydrogenChloride,HydrogenSulfide,IsoButane,IsoButene,Isohexane,Isopentane,Krypton,m-Xylene,MD2M,MD3M,MD4M,MDM,Methane,Methanol,MethylLinoleate,MethylLinolenate,MethylOleate,MethylPalmitate,MethylStearate,MM,n-Butane,n-Decane,n-Dodecane,n-Heptane,n-Hexane,n-Nonane,n-Octane,n-Pentane,n-Propane,n-Undecane,Neon,Neopentane,Nitrogen,NitrousOxide,Novec649,o-Xylene,OrthoDeuterium,OrthoHydrogen,Oxygen,p-Xylene,ParaDeuterium,ParaHydrogen,Propylene,Propyne,R11,R113,R114,R115,R116,R12,R123,R1233zd(E),R1234yf,R1234ze(E),R1234ze(Z),R124,R1243zf,R125,R13,R134a,R13I1,R14,R141b,R142b,R143a,R152A,R161,R21,R218,R22,R227EA,R23,R236EA,R236FA,R245ca,R245fa,R32,R365MFC,R40,R404A,R407C,R41,R410A,R507A,RC318,SES36,SulfurDioxide,SulfurHexafluoride,Toluene,trans-2-Butene,Water,Xenon
Copy C2 and paste result as value here ==> | 1-Butene | Acetone | Air | Ammonia | Argon | Benzene | CarbonDioxide | CarbonMonoxide | CarbonylSulfide | cis-2-Butene | CycloHexane | Cyclopentane | CycloPropane | D4 | D5 | D6 | Deuterium | Dichloroethane | DiethylEther | DimethylCarbonate | DimethylEther | Ethane | Ethanol | EthylBenzene | Ethylene | EthyleneOxide | Fluorine | HeavyWater | Helium | HFE143m | Hydrogen | HydrogenChloride | HydrogenSulfide | IsoButane | IsoButene | Isohexane | Isopentane | Krypton | m-Xylene | MD2M | MD3M | MD4M | MDM | Methane | Methanol | MethylLinoleate | MethylLinolenate | MethylOleate | MethylPalmitate | MethylStearate | MM | n-Butane | n-Decane | n-Dodecane | n-Heptane | n-Hexane | n-Nonane | n-Octane | n-Pentane | n-Propane | n-Undecane | Neon | Neopentane | Nitrogen | NitrousOxide | Novec649 | o-Xylene | OrthoDeuterium | OrthoHydrogen | Oxygen | p-Xylene | ParaDeuterium | ParaHydrogen | Propylene | Propyne | R11 | R113 | R114 | R115 | R116 | R12 | R123 | R1233zd(E) | R1234yf | R1234ze(E) | R1234ze(Z) | R124 | R125 | R13 | R134a | R13I1 | R14 | R141b | R142b | R143a | R152A | R161 | R21 | R218 | R22 | R227EA | R23 | R236EA | R236FA | R245ca | R245fa | R32 | R365MFC | R40 | R404A | R407C | R41 | R410A | R507A | RC318 | SES36 | SulfurDioxide | SulfurHexafluoride | Toluene | trans-2-Butene | Water | Xenon
Select C3 and convert text to columns.
|  | PureFluids |  | PredefinedMixtures |  | ParameterList |  | FluidType
Copy C3:n3 and paste here Transposed ==> |  | 1-Butene |  | Air.mix |  | A |  | PureFluids
This makes a list we can use in a dropdown. |  | Acetone |  | Amarillo.mix |  | ACENTRIC |  | PredefinedMixtures
|  | Air |  | Ekofisk.mix |  | ALPHA0
The same procedure can be used to extract |  | Ammonia |  | GulfCoast.mix |  | ALPHAR
the PredefinedMixtures list and the |  | Argon |  | GulfCoastGas(NIST1).mix |  | BVIRIAL
ParameterList. |  | Benzene |  | HighCO2.mix |  | Bvirial
|  | CarbonDioxide |  | HighN2.mix |  | C
|  | CarbonMonoxide |  | NaturalGasSample.mix |  | CONDUCTIVITY
|  | CarbonylSulfide |  | R401A.mix |  | CP0MASS
|  | cis-2-Butene |  | R401B.mix |  | CP0MOLAR
|  | CycloHexane |  | R401C.mix |  | CPMASS
|  | Cyclopentane |  | R402A.mix |  | CPMOLAR
|  | CycloPropane |  | R402B.mix |  | CVIRIAL
|  | D4 |  | R403A.mix |  | CVMASS
|  | D5 |  | R403B.mix |  | CVMOLAR
|  | D6 |  | R404A.mix |  | Cp0mass
|  | Deuterium |  | R405A.mix |  | Cp0molar
|  | Dichloroethane |  | R406A.mix |  | Cpmass
|  | DiethylEther |  | R407A.mix |  | Cpmolar
|  | DimethylCarbonate |  | R407B.mix |  | Cvirial
|  | DimethylEther |  | R407C.mix |  | Cvmass
|  | Ethane |  | R407D.mix |  | Cvmolar
|  | Ethanol |  | R407E.mix |  | D
|  | EthylBenzene |  | R407F.mix |  | DALPHA0_DDELTA_CONSTTAU
|  | Ethylene |  | R408A.mix |  | DALPHA0_DTAU_CONSTDELTA
|  | EthyleneOxide |  | R409A.mix |  | DALPHAR_DDELTA_CONSTTAU
|  | Fluorine |  | R409B.mix |  | DALPHAR_DTAU_CONSTDELTA
|  | HeavyWater |  | R410A.mix |  | DBVIRIAL_DT
|  | Helium |  | R410B.mix |  | DCVIRIAL_DT
|  | HFE143m |  | R411A.mix |  | DELTA
|  | Hydrogen |  | R411B.mix |  | DIPOLE_MOMENT
|  | HydrogenChloride |  | R412A.mix |  | DMASS
|  | HydrogenSulfide |  | R413A.mix |  | DMOLAR
|  | IsoButane |  | R414A.mix |  | Delta
|  | IsoButene |  | R414B.mix |  | Dmass
|  | Isohexane |  | R415A.mix |  | Dmolar
|  | Isopentane |  | R415B.mix |  | FH
|  | Krypton |  | R416A.mix |  | FRACTION_MAX
|  | m-Xylene |  | R417A.mix |  | FRACTION_MIN
|  | MD2M |  | R417B.mix |  | FUNDAMENTAL_DERIVATIVE_OF_GAS_DYNAMICS
|  | MD3M |  | R417C.mix |  | G
|  | MD4M |  | R418A.mix |  | GAS_CONSTANT
|  | MDM |  | R419A.mix |  | GMASS
|  | Methane |  | R419B.mix |  | GMOLAR
|  | Methanol |  | R420A.mix |  | GWP100
|  | MethylLinoleate |  | R421A.mix |  | GWP20
|  | MethylLinolenate |  | R421B.mix |  | GWP500
|  | MethylOleate |  | R422A.mix |  | Gmass
|  | MethylPalmitate |  | R422B.mix |  | Gmolar
|  | MethylStearate |  | R422C.mix |  | H
|  | MM |  | R422D.mix |  | HH
|  | n-Butane |  | R422E.mix |  | HMASS
|  | n-Decane |  | R423A.mix |  | HMOLAR
|  | n-Dodecane |  | R424A.mix |  | Hmass
|  | n-Heptane |  | R425A.mix |  | Hmolar
|  | n-Hexane |  | R426A.mix |  | I
|  | n-Nonane |  | R427A.mix |  | ISOBARIC_EXPANSION_COEFFICIENT
|  | n-Octane |  | R428A.mix |  | ISOTHERMAL_COMPRESSIBILITY
|  | n-Pentane |  | R429A.mix |  | L
|  | n-Propane |  | R430A.mix |  | M
|  | n-Undecane |  | R431A.mix |  | MOLARMASS
|  | Neon |  | R432A.mix |  | MOLAR_MASS
|  | Neopentane |  | R433A.mix |  | MOLEMASS
|  | Nitrogen |  | R433B.mix |  | O
|  | NitrousOxide |  | R433C.mix |  | ODP
|  | Novec649 |  | R434A.mix |  | P
|  | o-Xylene |  | R435A.mix |  | PCRIT
|  | OrthoDeuterium |  | R436A.mix |  | PH
|  | OrthoHydrogen |  | R436B.mix |  | PHASE
|  | Oxygen |  | R437A.mix |  | PIP
|  | p-Xylene |  | R438A.mix |  | PMAX
|  | ParaDeuterium |  | R439A.mix |  | PMIN
|  | ParaHydrogen |  | R440A.mix |  | PRANDTL
|  | Propylene |  | R441A.mix |  | PTRIPLE
|  | Propyne |  | R442A.mix |  | P_CRITICAL
|  | R11 |  | R443A.mix |  | P_MAX
|  | R113 |  | R444A.mix |  | P_MIN
|  | R114 |  | R444B.mix |  | P_REDUCING
|  | R115 |  | R445A.mix |  | P_TRIPLE
|  | R116 |  | R446A.mix |  | P_max
|  | R12 |  | R447A.mix |  | P_min
|  | R123 |  | R448A.mix |  | Pcrit
|  | R1233zd(E) |  | R449A.mix |  | Phase
|  | R1234yf |  | R449B.mix |  | Prandtl
|  | R1234ze(E) |  | R450A.mix |  | Q
|  | R1234ze(Z) |  | R451A.mix |  | RHOCRIT
|  | R124 |  | R451B.mix |  | RHOMASS_CRITICAL
|  | R125 |  | R452A.mix |  | RHOMASS_REDUCING
|  | R13 |  | R453A.mix |  | RHOMOLAR_CRITICAL
|  | R134a |  | R454A.mix |  | RHOMOLAR_REDUCING
|  | R13I1 |  | R454B.mix |  | S
|  | R14 |  | R500.mix |  | SMASS
|  | R141b |  | R501.mix |  | SMOLAR
|  | R142b |  | R502.mix |  | SMOLAR_RESIDUAL
|  | R143a |  | R503.mix |  | SPEED_OF_SOUND
|  | R152A |  | R504.mix |  | SURFACE_TENSION
|  | R161 |  | R507A.mix |  | Smass
|  | R21 |  | R508A.mix |  | Smolar
|  | R218 |  | R508B.mix |  | Smolar_residual
|  | R22 |  | R509A.mix |  | T
|  | R227EA |  | R510A.mix |  | TAU
|  | R23 |  | R511A.mix |  | TCRIT
|  | R236EA |  | R512A.mix |  | TMAX
|  | R236FA |  | R513A.mix |  | TMIN
|  | R245ca |  | TypicalNaturalGas.mix |  | TTRIPLE
|  | R245fa |  |  |  | T_CRITICAL
|  | R32 |  |  |  | T_FREEZE
|  | R365MFC |  |  |  | T_MAX
|  | R40 |  |  |  | T_MIN
|  | R404A |  |  |  | T_REDUCING
|  | R407C |  |  |  | T_TRIPLE
|  | R41 |  |  |  | T_critical
|  | R410A |  |  |  | T_freeze
|  | R507A |  |  |  | T_max
|  | RC318 |  |  |  | T_min
|  | SES36 |  |  |  | T_reducing
|  | SulfurDioxide |  |  |  | T_triple
|  | SulfurHexafluoride |  |  |  | Tau
|  | Toluene |  |  |  | Tcrit
|  | trans-2-Butene |  |  |  | Tmax
|  | Water |  |  |  | Tmin
|  | Xenon |  |  |  | Ttriple
U
UMASS
UMOLAR
Umass
Umolar
V
VISCOSITY
Z
acentric
alpha0
alphar
conductivity
dBvirial_dT
dCvirial_dT
dalpha0_ddelta_consttau
dalpha0_dtau_constdelta
dalphar_ddelta_consttau
dalphar_dtau_constdelta
dipole_moment
fraction_max
fraction_min
fundamental_derivative_of_gas_dynamics
gas_constant
isobaric_expansion_coefficient
isothermal_compressibility
molar_mass
molarmass
molemass
p_critical
p_reducing
p_triple
pcrit
pmax
pmin
ptriple
rhocrit
rhomass_critical
rhomass_reducing
rhomolar_critical
rhomolar_reducing
speed_of_sound
surface_tension
viscosity