## Terms of Use
(c) University of Innsbruck, Unit of Energy Efficient Building
Technikerstrasse 13, A-6020 Innsbruck, Austria
Wolfgang Streicher
wolfgang.streicher@uibk.ac.at
Inputs: Only | yellow fields | can be changed, the rest is closed
Exception: Worksheet "Materials and Climate". Here more materials and climates can be attached but stick to the same format.
Every new Material or new climate must be a new row.
FREEWARE: but please cite when it is used
It is NOT allowed to sell this software commercially
If you use plots make sure that the citation of the University of Innsbruck is readable or attached to the graph
There is NO liabilty for the use, calculation and the results
There is no support team behind the tools, please ask only in very urgent situations
Do not forget to harmonize inout data (e.g. when calculating Glaser for hot/cold situation increase indoor air temperature and humidity for hot, decrease both in cold situation.

## U_value_Glaser_wall
Wall / Roof /Floor
Input | Outside | Layer 1 | Layer 2 | Layer 3 | Layer 4 | Inside
Material (Pull down) |  | Plaster | Brick heavy | Mineralw. | Plaster
Thickness s |  | 0.01 | 0.2 | 0.15 | 0.01 |  | m
Therm. conduct. k |  | 0.9 | 0.6 | 0.04 | 0.9 |  | W/mk
Diff.res.fact μ |  | 13 | 12 | 1 | 13 |  | -
alpha αo | 14 | W/m²K |  |  | αi | 7 | W/m²K
Climate | Innsbruck / Austria |  | Month | Feb
T_out/in T0 | 0.8 | °C |  |  | Ti | 21 | °C
rel. hum. jo | 75 | % |  |  | ji | 35 | %
Output | [5 empty] | Total
Position |  | 0 | 0.01 | 0.21 | 0.36 | 0.37 | m
R_Layers 1/α, d/λ | 0.071429 | 0.011111 | 0.33333 | 3.75 | 0.011111 | 0.14286 | m²K/W
sum R | [5 empty] | 4.3198 | m²K/W
U_i (von R) 1/sum R | [5 empty] | 0.23149 | W/m²K
U_i (from long fomula) | [5 empty] | 0.23149 | W/m²K
Total Heat Transfer Qtot | [5 empty] | 4.6761 | W/m²
Water Vapor Diffussion
sd |  | 0.13 | 2.4 | 0.15 | 0.13 |  | m
1/Δ; 1/ß | 1499.2504 | 180700 | 3336000 | 208500 | 180700 | 8000 | m²hPa/kg
1/Δ total | 1499.2504 | 182199.2504 | 3518199.2504 | 3726699.2504 | 3907399.2504 | 3915399.2504 | m²hPa/kg
g /Diffflow | [5 empty] | 9.8225e-05 | kg/m²h
Position | Outside | o/L1 | L1/L2 | L2/L3 | L3/L4 | L4/i | Inside
Position in wall | -0.037 | 0 | 0.01 | 0.21 | 0.36 | 0.37 | 0.407 | m
Temperature | 0.8 | 1.134 | 1.186 | 2.7447 | 20.28 | 20.332 | 21 | °C
p_Saturation | 647.6387 | 663.4918 | 665.9882 | 744.8047 | 2378.9533 | 2386.5846 | 2486.6279 | Pa
p_Real | 485.7291 | 485.8763 | 503.6256 | 831.3047 | 851.7847 | 869.534 | 870.3198 | Pa
1/Δ total | 0 | 1499.2504 | 182199.2504 | 3518199.2504 | 3726699.2504 | 3907399.2504 | 3915399.2504 | m²hPa/kg
Sd total | -0.0009995 | 0 | 0.13 | 2.53 | 2.68 | 2.81 | 2.8153 | m²hPa/kg
Layer-Linies | Temperatures |  | Vapor pressure
| 22 | -0.2 | 2686.5846 | 185.7291 | 2686.5846 | 185.7291
Outside | 0 | 0 | 0 | 0 | 0 | 0
L1/2 | 0.01 | 0.01 | 0.01 | 0.01 | 0.13 | 0.13
L2/3 | 0.21 | 0.21 | 0.21 | 0.21 | 2.53 | 2.53
L3/4 | 0.36 | 0.36 | 0.36 | 0.36 | 2.68 | 2.68
Inside | 0.37 | 0.37 | 0.37 | 0.37 | 2.81 | 2.81
[8 empty] | o | o/L1 | L1/L2 | L2/L3 | L3/L4 | L4/i | i
| Outside |  | Inside |  |  | Position | m | -0.037 | 0 | 0.01 | 0.21 | 0.36 | 0.37 | 0.407
| Temp | rel. hum. | Temp | rel. hum. |  |  | Qtot | Temperature
| °C | % | °C | % |  |  | W/m² | °C | °C | °C | °C | °C | °C | °C
Jan | -1.3 | 82 | 21 | 35 |  | Jan | 5.1622 | -1.3 | -0.93127 | -0.87391 | 0.84683 | 20.2052 | 20.2625 | 21
Feb | 0.8 | 75 | 21 | 35 |  | Feb | 4.6761 | 0.8 | 1.134 | 1.186 | 2.7447 | 20.28 | 20.332 | 21
Mar | 5.6 | 68 | 21 | 35 |  | Mar | 3.5649 | 5.6 | 5.8546 | 5.8942 | 7.0826 | 20.4511 | 20.4907 | 21
Apr | 10.3 | 63 | 21 | 35 |  | Apr | 2.4769 | 10.3 | 10.4769 | 10.5044 | 11.3301 | 20.6186 | 20.6462 | 21
May | 14.4 | 66 | 21 | 35 |  | May | 1.5278 | 14.4 | 14.5091 | 14.5261 | 15.0354 | 20.7648 | 20.7817 | 21
Jun | 17.9 | 67 | 21 | 35 |  | Jun | 0.71762 | 17.9 | 17.9513 | 17.9592 | 18.1984 | 20.8895 | 20.8975 | 21
July | 18.9 | 69 | 21 | 35 |  | July | 0.48613 | 18.9 | 18.9347 | 18.9401 | 19.1022 | 20.9252 | 20.9306 | 21
Aug | 18.5 | 71 | 21 | 35 |  | Aug | 0.57872 | 18.5 | 18.5413 | 18.5478 | 18.7407 | 20.9109 | 20.9173 | 21
Sept | 14.2 | 75 | 21 | 35 |  | Sept | 1.5741 | 14.2 | 14.3124 | 14.3299 | 14.8546 | 20.7576 | 20.7751 | 21
Oct | 10 | 76 | 21 | 35 |  | Oct | 2.5464 | 10 | 10.1819 | 10.2102 | 11.059 | 20.6079 | 20.6362 | 21
Nov | 4.4 | 80 | 21 | 35 |  | Nov | 3.8427 | 4.4 | 4.6745 | 4.7172 | 5.9981 | 20.4083 | 20.451 | 21
Dec | -0.1 | 83 | 21 | 35 |  | Dec | 4.8844 | -0.1 | 0.24889 | 0.30316 | 1.9313 | 20.248 | 20.3022 | 21
[8 empty] | o | o/L1 | L1/L2 | L2/L3 | L3/L4 | L4/i | i | o | o/L1 | L1/L2 | L2/L3 | L3/L4 | L4/i | i
[6 empty] | g/Diffflow |  | Psaturated | [6 empty] | Preal
[7 empty] | kg/m²h | Pa | Pa | Pa | Pa | Pa | Pa | Pa | Pa | Pa | Pa | Pa | Pa | Pa | Pa
[6 empty] | Jan | 0.00010598 | 555.3454 | 570.6634 | 573.0791 | 649.8413 | 2367.9972 | 2376.3892 | 2486.6279 | 455.3832 | 455.5421 | 474.6919 | 828.2263 | 850.3222 | 869.472 | 870.3198
[6 empty] | Feb | 9.8225e-05 | 647.6387 | 663.4918 | 665.9882 | 744.8047 | 2378.9533 | 2386.5846 | 2486.6279 | 485.7291 | 485.8763 | 503.6256 | 831.3047 | 851.7847 | 869.534 | 870.3198
[6 empty] | Mar | 6.4142e-05 | 910.5573 | 926.7966 | 929.3453 | 1008.7175 | 2404.1626 | 2410.0325 | 2486.6279 | 619.179 | 619.2751 | 630.8656 | 844.8426 | 858.2162 | 869.8066 | 870.3198
[6 empty] | Apr | 2.0484e-05 | 1254.1562 | 1269.0504 | 1271.3811 | 1343.0685 | 2429.0729 | 2433.1869 | 2486.6279 | 790.1184 | 790.1491 | 793.8505 | 862.1837 | 866.4545 | 870.1559 | 870.3198
[6 empty] | May | -5.4438e-05 | 1641.6172 | 1653.2213 | 1655.0329 | 1710.1929 | 2450.9874 | 2453.5443 | 2486.6279 | 1083.4674 | 1083.3857 | 1073.5487 | 891.9427 | 880.5923 | 870.7553 | 870.3198
[6 empty] | Jun | -0.00012877 | 2051.4819 | 2058.0954 | 2059.1258 | 2090.2496 | 2469.8315 | 2471.0403 | 2486.6279 | 1374.4929 | 1374.2998 | 1351.0317 | 921.4659 | 894.618 | 871.3499 | 870.3198
[6 empty] | July | -0.00016258 | 2183.9196 | 2188.6497 | 2189.3862 | 2211.5852 | 2475.2388 | 2476.0592 | 2486.6279 | 1506.9045 | 1506.6608 | 1477.2817 | 934.8985 | 900.9995 | 871.6204 | 870.3198
[6 empty] | Aug | -0.00016398 | 2130.073 | 2135.5833 | 2136.4416 | 2162.3309 | 2473.0747 | 2474.0506 | 2486.6279 | 1512.3518 | 1512.106 | 1482.4755 | 935.4511 | 901.2621 | 871.6316 | 870.3198
[6 empty] | Sept | -8.8135e-05 | 1620.5357 | 1632.3582 | 1634.204 | 1690.4348 | 2449.9144 | 2452.5478 | 2486.6279 | 1215.4018 | 1215.2697 | 1199.3437 | 905.3268 | 886.9508 | 871.0248 | 870.3198
[6 empty] | Oct | -1.6323e-05 | 1229.2505 | 1244.2982 | 1246.6533 | 1319.148 | 2427.4761 | 2431.7032 | 2486.6279 | 934.2303 | 934.2059 | 931.2563 | 876.8032 | 873.3999 | 870.4504 | 870.3198
[6 empty] | Nov | 5.1196e-05 | 837.3342 | 853.6117 | 856.1684 | 936.0561 | 2397.8384 | 2404.1517 | 2486.6279 | 669.8674 | 669.9441 | 679.1952 | 849.9848 | 860.6591 | 869.9102 | 870.3198
[6 empty] | Dec | 9.3701e-05 | 606.5601 | 622.2053 | 624.6704 | 702.715 | 2374.2524 | 2382.2105 | 2486.6279 | 503.4449 | 503.5854 | 520.5171 | 833.1019 | 852.6385 | 869.5702 | 870.3198
[9 empty] | o/L1 | L1/L2 | L2/L3 | L3/L4 | L4/i |  |  | o/L1 | L1/L2 | L2/L3 | L3/L4 | L4/i
[9 empty] | Moisture Content | [6 empty] | Moisture in-out
[8 empty] | Day/month | kg/m² | [6 empty] | kg/m²,month
[7 empty] | Oct | 31 | 0 | 0 | 0 | 0 | 0 |  |  | -153.8705 | -1.3508 | -0.9221 | -6.4376 | -145.4938
[7 empty] | Nov | 30 | 0 | 0 | 0 | 0 | 0 |  |  | -88.2413 | -0.73348 | -0.17364 | -6.1622 | -138.3644
[7 empty] | Dec | 31 | 0 | 0 | 0.2718 | 0 | 0 |  |  | -58.9346 | -0.44606 | 0.2718 | -6.3031 | -140.9636
[7 empty] | Jan | 31 | 0 | 0 | 0.64366 | 0 | 0 |  |  | -57.2076 | -0.42137 | 0.37186 | -6.2868 | -140.4302
[7 empty] | Feb | 28 | 0 | 0 | 0.80653 | 0 | 0 |  |  | -79.6776 | -0.62806 | 0.16287 | -5.7139 | -127.6932
[7 empty] | Mar | 31 | 0 | 0 | 0.46492 | 0 | 0 |  |  | -152.6546 | -1.2783 | -0.34161 | -6.4039 | -143.5343
[7 empty] | Apr | 30 | 0 | 0 | 0 | 0 | 0 |  |  | -230.0023 | -1.9792 | -0.97011 | -6.2642 | -140.9608
[7 empty] | May | 31 | 0 | 0 | 0 | 0 | 0 |  |  | -282.7393 | -2.4903 | -1.7057 | -6.5052 | -147.5008
[7 empty] | Jun | 30 | 0 | 0 | 0 | 0 | 0 |  |  | -328.2933 | -2.9348 | -2.3578 | -6.3147 | -144.2669
[7 empty] | July | 31 | 0 | 0 | 0 | 0 | 0 |  |  | -338.3147 | -3.0498 | -2.6614 | -6.5211 | -149.5183
[7 empty] | Aug | 31 | 0 | 0 | 0 | 0 | 0 |  |  | -309.2774 | -2.8008 | -2.5575 | -6.5111 | -149.3301
[7 empty] | Sept | 30 | 0 | 0 | 0 | 0 | 0 |  |  | -200.2391 | -1.8023 | -1.5838 | -6.2656 | -142.6285
[7 empty] | Oct | 31 | 0 | 0 | 0 | 0 | 0 |  |  | -153.8705 | -1.3508 | -0.9221 | -6.4376 | -145.4938
[7 empty] | Nov | 30 | 0 | 0 | 0 | 0 | 0 |  |  | -88.2413 | -0.73348 | -0.17364 | -6.1622 | -138.3644
αi
s2
k2
s3
αo
k3
k4
k1
s1
s4
T0
φo
o/L1
L1/L2
L2/L3
L3/L4
L4/i
L1
L2
L3
L4
Out-side
In-side
R0
R1
R2
R3
R4
Ri
Ti
φi
μ0
μ1
μ2
μ3
μ4
μi
(c) Unit Energy Efficient Building, University of Innsbruck
(c) Unit Energy Efficient Building, University of Innsbruck
Position
(c) Unit Energy Efficient Building
University of Innsbruck
𝑄 ̇=𝑈⋅𝐴⋅Δ𝑇_𝑡𝑜𝑡𝑎𝑙=𝛼_𝑖⋅𝐴⋅(𝑡_𝑖−𝑡_(𝑤,𝑖) )=𝑘_𝑛/𝑠_𝑛 𝐴⋅(𝑡_(𝑛−1)−𝑡_𝑛 )=𝛼_0⋅𝐴⋅(𝑡_(𝑤,𝑎)−𝑡_𝑎 ) Δ𝑇_𝑡𝑜𝑡𝑎𝑙=𝑄 ̇/𝑈 (𝑡_𝑖−𝑡_(𝑤,𝑖) )=𝑄 ̇/𝛼_𝑖 (𝑡_(𝑛−1)−𝑡_𝑛 )=𝑄 ̇/(𝑘_𝑛/𝑠_𝑛 ) (𝑡_(𝑤,𝑎)−𝑡_𝑎 )=𝑄 ̇/𝛼_0 Δ𝑇_𝑡𝑜𝑡𝑎𝑙=∑▒Δ𝑇 𝑄 ̇/𝑈=𝑄 ̇/𝛼_𝑖 +𝑄 ̇/(∑_𝑛▒𝑘_𝑛/𝑠_𝑛 )+𝑄 ̇/𝛼_𝑜 1/𝑈=1/𝛼_𝑖 +" " ∑_𝑛▒𝑠_𝑛/𝑘_𝑛 + 1/𝛼_𝑜 " " 𝑅=𝑅_𝑖+∑_𝑛▒𝑅_𝑛 "+ " 𝑅_a
Feb
Note on B8: Streicher, Wolfgang: if Hot/Cold is chosen: Jan = Cold month Feb = Hot month

## Materials_Climate
Material |  |  | Climate Monthly Average
| Thermal Conductivity | Diffusion resistance |  | Temperatuere [°C] | [12 empty] | Rel Humidity [%]
Name | λ [W/mK] | μ [-] | Location | Jan | Feb | Mar | Apr | May | Jun | July | Aug | Sept | Oct | Nov | Dec | Spalte2 | Jan3 | Feb4 | Mar5 | Apr6 | May7 | Jun8 | July9 | Aug10 | Sept11 | Oct12 | Nov13 | Dec14
Plaster | 0.9 | 13 | Hot/Humid Gautam | 13.8 | 16.7 | 22.1 | 27.5 | 29.1 | 29.8 | 28 | 28.2 | 27.2 | 25.7 | 20.4 | 15.8 |  | 79 | 77 | 57 | 45 | 58 | 70 | 88 | 86 | 88 | 79 | 77.5 | 79
XPS | 0.04 | 150 | Mild Kathmandu | 9.8 | 12 | 16 | 19 | 21 | 23 | 23 | 22.8 | 22 | 19 | 14 | 10.3 |  | 76 | 72 | 64 | 56 | 75 | 83 | 89 | 89 | 93 | 84 | 76 | 82
Mineralw. | 0.04 | 1 | Cold Jumla | -5.4 | -2.85 | 0.35 | 3.8 | 8.5 | 11.3 | 12.9 | 12.7 | 11.5 | 6.4 | 2.75 | -1.8 |  | 54 | 70 | 65 | 70 | 76 | 84 | 90 | 90 | 87 | 75 | 60 | 45.5
Cork | 0.04 | 10 | Innsbruck / Austria | -1.3 | 0.8 | 5.6 | 10.3 | 14.4 | 17.9 | 18.9 | 18.5 | 14.2 | 10 | 4.4 | -0.1 |  | 82 | 75 | 68 | 63 | 66 | 67 | 69 | 71 | 75 | 76 | 80 | 83
Air 5 cm↕ | 0.29 | 1 | Hot/Cold | -20 | 35 | [10 empty] | Rel Humidity [%] Jan3: 80; Rel Humidity [%] Feb4: 80
Brick heavy | 0.6 | 12
Brick poros | 0.25 | 7
BrickPoroth | 0.12 | 7
Concrete | 2.1 | 120
Wood | 0.13 | 40
Vap.Bar.tight | 0.17 | 40000
Vap.Bar.red. | 0.17 | 9
Vap. Bar.med | 0.17 | 200
Note on C3: Beck, Simon: Wärmeleitfähigkeit in W/mK
Note on D3: Beck, Simon: Diffusionswiderstandsfaktor dimensionlos

## U_value_tube
Insulated Tube
Convection and Radiation Outside
DN (outer diameter tube) | 0.1 | m
s_tube (wall thickness tube) | 0.002 | m
lam_tube (heat conductivity tube, k-value) | 250 | W/mk
s_inslulation (thickness insulation) | 0.05 | m
lam_insulation (heat conductivity insul) | 0.04 | W/mK
Alpha_i (heat transfer coefficient tube fluid) | 500 | W/m²K
Alpha_o (heat transfer coefficient ambient) | 14 | W/m²K
Output
di | 0.096 | m
d insul_out | 0.2 | m
dm_tube | 0.097986 | m
dm_insul | 0.14427 | m
Ri=1/alpha_i | 0.002 | m²K/W
R_tube | 7.8378e-06 | m²K/W
R_Insul | 0.83178 | m²K/W
Ra=1/alpha_o | 0.034286 | m²K/W
sum R | 0.86807 | m²K/W
U_i (from R) | 1.152 | W/m²K
U_i (from long fomula) | 1.152 | W/m²K
αi
dinsul_out
λ(j)
di
DN
αa

## heat exchanger
[9 empty] | 120 | kg
Heat exchanger INPUT |  |  |  | Results |  |  |  |  | 10 | Minuten
T_hot _inlet | 55 | °C | [6 empty] | 600 | s
T_cold_inlet | 10 | °C |  |  | in | out |  | qdot | 0.2 | kg/s
m_dot_hot | 0.1667 | kg/s |  | thot_par | 55 | 30.684 |  | -16943.5641 | 25.08 | kW
m_dot_cold | 0.2 | kg/s |  | tcold_par | 10 | 30.2674 |  | 16943.5641
cp_hot | 4180 | J/kgK
cp_cold | 4180 | J/kgK | [5 empty] | qdot
U | 500 | W/m²K |  | qdot | 0 | 16943.5641 | 25081.5911
A | 4.27 | m² | parallel | thot_par | 55 | 30.684
|  |  |  | tcold_par | 10 | 30.2674
Calculation |  |  | counter | thot_counter | 55 | 30.684 | 19.0049 | -25081.5911 | counter flow
C_hot | 696.806 | J/sK |  | tcold, counter | 40.0019 | 19.7345 | 10 | 25081.5911
C_cold | 836 | J/sK
C_min | 696.806 | J/sK
C_R | 0.8335 | -
NTU_hot | 3.064 | - | [6 empty] | parallel flow
NTU_cold | 2.5538 | -
NTU | 3.064 | -
Counter Flow
Effectiv_C_min | 0.79989 | -
T_cold_out | 40.0019 | °C | 0.51015
T_hot_out | 19.0049 | °C
Effectiv_hot_counter | 0.79989 | -
Effectiv_cold_counter | 0.66671
Tlog_counter | 11.7478 | °C
Parallel Flow
Effectiv_cold_parallel | 0.54036 | -
T_cold_out | 30.2674 | °C
T_hot_out | 30.684 | °C
Effectiv_hot_parallel | 0.54036 | - | 0.45406
Tlog_parallel | 9.5214 | °C
Alternativ T_hin; T_hout gegeben
T_hot_outlet | 50 | °C
T_cin aus T_hin;T_hout | 48.7491 | °C

## combustion
Combustion Calculation
O2 in Air | 0.232 |  | Fuels - mass distribution
N2 in air | 0.768 |  | Methane | Hard Coal | Oil EL | Wood
c | 12 | Mass% | 60% | 77% | 85% | 37% |  | 35
h | 2 | Mass% | 40% | 5% | 15% | 5% |  | 4
o (O2) 2*16 | 32 | Mass% | 0% | 8% | 0% | 32% |  | 30
n (N2) 2*14 | 28 | Mass% | 0% | 1% | 0% | 0% |  | 0
s | 32 | Mass% | 0% | 1% | 0% | 0% |  | 0
w | 36 | Mass% | 0% | 3% | 0% | 25% |  | 30
Ash |  | Mass% | 0% | 5% | 2.776e-15% | 1% |  | 13578
Lambda |  |  | 1 | 1 | 1.5 | 1
O2min |  | kgO2/kgfuel | 4.8 | 2.3833 | 3.4667 | 1.0667
Lmin |  | kgair/kg fuel | 20.6897 | 10.273 | 14.9425 | 4.5977
|  | m³air/kgfuel | 15.981 | 7.935 | 11.5418 | 3.5513
N2min |  | kgN2/kgfuel | 15.869 | 7.8794 | 11.4609 | 3.5264
Rw,min |  | kgfg/kgfuel | 21.669 | 11.2127 | 15.9276 | 5.5831
m³fg/kgfuel
Rdry,min
L |  | kgair/kg fuel | 20.6897 | 10.273 | 22.4138 | 4.5977
LHV |  | kJ/kg | 35790 | 30746.7 | 43690.25 | 13516.45
HHV |  | kJ/kg | 39850 | 31912.14 | 46968.05 | 15216.05 | only for solid and liquid fuels
Flue gas components
Wet flue gas
μCO2 |  | kg/kgfuel | 2.2 | 2.8233 | 3.1167 | 1.3567
μSO2 |  | kg/kgfuel | 0 | 0.02 | 0 | 0
μAr |  | kg/kgfuel
μH20 |  | kg/kgfuel | 3.6 | 0.48 | 1.35 | 0.7
μO2 |  | kg/kgfuel | 0 | 0 | 1.7333 | 0
μN2 |  | kg/kgfuel | 15.869 | 7.8894 | 17.1914 | 3.5264
total |  | kg/kgfuel | 21.669 | 11.2127 | 23.3914 | 5.5831
Dry flue gas |  | kg/kgfuel | 18.069 | 10.7327 | 22.0414 | 4.8831
λ*lmin+(1-a) |  |  | 21.6897 | 11.223 | 23.4138 | 5.5877
wCO2 |  | kg/kgfg | 0.10143 | 0.25157 | 0.13311 | 0.2428
wSO2 |  | kg/kgfg | 0 | 0.0017821 | 0 | 0
wAr |  | kg/kgfg | 0.01221 | 0.011717 | 0.012253 | 0.010532
wH20 |  | kg/kgfg | 0.16598 | 0.042769 | 0.057658 | 0.12528
wO2 |  | kg/kgfg | 0 | 0 | 0.07403 | 0
wN2 |  | kg/kgfg | 0.73164 | 0.70297 | 0.73424 | 0.63111
total without Ar |  | kg/kgfg | 0.99905 | 0.99908 | 0.99904 | 0.99918
VCO2 |  | m³/kgfuel | 1.1205 | 1.438 |  | 0.69098
VSO2 |  | m³/kgfuel | 0 | 0.0070031 | 0 | 0
VAr |  | m³/kgfuel
VH20 |  | m³/kgfuel | 4.482 | 0.5976 | 1.6807 | 0.8715
VO2 |  | m³/kgfuel | 0 | 0 | 1.2139 | 0
VN2 |  | m³/kgfuel | 12.2574 | 6.0941 | 13.2789 | 2.7239
total |  | m³/kgfuel | 17.8599 | 8.1367 | 16.1735 | 4.2863
cp_Flue Gas |  | kJ/kgK | 1.3 | 1.3 | 1.3 | 1.3
Tflame |  | °C | 1269.3041 | 2098.0513 | 1435.3883 | 1857.4177
kg air/kgfuel